Table 1: Read Dates & Incubation Observation

| ETX Submission ID | Set-up Analyst & Date | Sampling Site & Location | Plate Reading Analyst (≥ 48H) | CFUs Observed after 48 Hour Incubation at 30–35°C (E001031) | Plate Reading Analyst (NLT 5 days) | CFUs Observed after NLT 5-day Incubation at 20–25°C (E001034) | Microbial Identification |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ETX-260518-0254 | SMO 07MAY 2026 | Active air sampling plate | SAS | 504 CFUs on active air sample plate | SAS | 748 CFUs on active air sample plate | Kocuria palustris |

Table 2: Environmental Monitoring for Analyst & Cleanroom

| Environmental Monitoring (EM) Sampling Site | Frequency | Date (DDMMM YYYY) | Analyst (Initials) | Day /Week(s) | Observation* | Environmental Monitoring Plate ETX ID | Microbial ID | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Weekly Active Air Sampling Bracketing 116 |  |  |  |  |  |  |  |  |
| Active Air Sampling of Cleanrooms | Weekly | 29APR 2026 | SMO | Week Before Testing Date | No growth | N/A | N/A | None |
| Active Air Sampling of Cleanrooms | Weekly | 07MAY 2026 | SMO | Week of Testing Date | 748 CFUs in ISO 7 116A and 1 CFU in ISO 7 116B | ETX-260518-0254 ETX-260518-0256 | Kocuria palustris | None |
| Active Air Sampling of Cleanrooms | Weekly | 15MAY 2026 | SMO | Week After Testing Date | 6 CFUs in ISO 8 116 | ETX-260526-0428 | Gram (+) cocci Gram-variable coccobacilli | None |
| Surface Sampling of Anteroom and Cleanroom Bracketing 116 |  |  |  |  |  |  |  |  |
| Surface Sampling of Cleanrooms | Weekly | 29APR 2026 | SMO | Week Before Testing Date | No growth | N/A | N/A | None |
| Surface Sampling of Cleanrooms | Weekly | 07MAY 2026 | SMO | Week of Testing Date | No growth | N/A | N/A | None |
| Surface Sampling of Cleanrooms | Weekly | 15MAY 2026 | SMO | Week After Testing Date | 1 CFU on cart in ISO 8 116 and 2 CFUs on floor in 116A ISO 7 | ETX-260526-0442 ETX-260526-0448 | Gram (+) cocci Sporosarcina psychrophila Bacillus pumilus | None |