Table 1: Read Dates & Incubation Observation

| ETX Submission ID | Set-up Analyst & Date | Sampling Site & Location | Plate Reading Analyst (≥ 48H) | CFUs Observed after 48 Hour Incubation at 30–35°C (E001031) | Plate Reading Analyst (NLT 5 days) | CFUs Observed after NLT 5-day Incubation at 20–25°C (E001034) | Microbial Identification |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ETX-260526-0461 | SMO 08MAY 2026 | Active air sampling plate | MC | 0 CFU | SAS | 11 CFU in 115B ISO 7 sampling plate | Talaromyces purpurogenus |

Table 2: Environmental Monitoring for Analyst & Cleanroom

| Environmental Monitoring (EM) Sampling Site | Frequency | Date (DDMM YYYY) | Analyst (Initials) | Day /Week(s) | Observation* | Environmental Monitoring Plate ETX ID | Microbial ID | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Weekly Active Air Sampling Bracketing 115 |  |  |  |  |  |  |  |  |
| Active Air Sampling of Cleanrooms | Weekly | 29APR 2026 | SMO | Week (Before Testing Date | 1 CFU for 115 ISO 8 | ETX-260506-0280 | Micrococcus luteus | None |
| Active Air Sampling of Cleanrooms | Weekly | 08MAY 2026 | SMO | Week (On of Testing Date) | 1 CFU in 115A ISO 7 and 11 CFU in 115B ISO 7 | ETX-260518-0249 ETX-260518-0250 | Staphylococcus aureus Penicillium decumbens Cladosporium tenuissimum Cladosporium langeronii Cladosporium halotolerans | None |
| Active Air Sampling of Cleanrooms | Weekly | 14MAY 2026 | SMO | Week (On or After Testing Date) | 1 CFU in 115 ISO 8 and 11 CFU in 115B ISO 7 | ETX-260526-0391 ETX-260526-0395 | Gram (+) cocci Candida orthopsilosis Budding yeast | None |
| Surface Sampling of Anteroom and Cleanroom Bracketing 115 |  |  |  |  |  |  |  |  |
| Active Air Sampling of Cleanrooms | Weekly | 29APR 2026 | SMO | Week (Before Testing Date | No growth | N/A | N/A | None |
| Surface Sampling of Cleanrooms | Weekly | 08MAY 2026 | SMO | Week (On of Testing Date) | No growth | N/A | N/A | None |
| Surface Sampling of Cleanrooms | Weekly | 14MAY 2026 | SMO | Week (On or After Testing Date) | 1 CFU on table in ISO 8 115 and 1 CFU on the cart in 115 ISO 8 | ETX-260526-0424 ETX-260526-0425 | Gram (+) rods Staphylococcus capitis | None |